UNIVERSITY OF NAIROBI

SCHOOL OF ENGINEERING

DEPARTMENT OF ENVIRONMENTAL AND BIOSYSTEMS ENGINEERING

FEB 540: ENGINEERING DESIGN PROJECT REPORT

2017/2018 ACADEMIC YEAR

DESIGN OF WATER DISTRIBUTION SYSTEM THROUGH EPANET

CASE STUDY ARM, KALOLENI

CANDIDATE NAME:           CAXTON KITONGA NGUI

CANDIDATE No.:                  F21/1989/2013

COORDINATOR:                       MR. ALBERT KENYANI INIMA

A Report Submitted in Partial Fulfillment for the Requirements of the Degree of Bachelor of Science in Environmental and Biosystems Engineering, the University of Nairobi

DECLARATION

I declare that this project, except where specifically acknowledged, is my original work. This report has not been in whole or in part submitted for any degree or examination at any other University.

Caxton Kitonga Ngui-F21/1989/2013

Signature………………………. Date…………………………...

This project report has been submitted for examination with my approval as University Supervisor

Mr. Albert Kenyani Inima

Signature………………………. Date…………………………...

DEDICATION

I dedicate this Project to My Dad, Mr. Stephen Kinyilli, Mum, Mrs. Rhoda Wairimu, My brothers, Clinton, Ken, and Eric and to all my dear friends for their constant prayers and emotional support.

You all inspired me and gave me the strength to do this project to completion

ACKNOWLEDGEMENT

I am grateful to God Almighty for the strength throughout the five years I have been at the University.

I would like to sincerely thank my supervisor Mr. Albert kenyani Inima for his guidance and support throughout my design project. Without his assistance, ability to work this design project to completion would have been impossible.

Special thanks to ARM limited PLC employees for the information and the unwavering support during the design process. Thanks to Mr. Ephraim for suggesting to me that I should design for them this project.

This design project report would not have been realized without the support of my family, whose love and encouragement has always given me the confidence to believe in my own abilities and for the financial support in the development of this report. This design project report is dedicated to them.

To all those who contributed, my deepest gratitude

ABSTRACT

Water is the source of life for every living organism worldwide. In Kenya, the available water resources are diminishing at an alarming rate with an estimate that by the year 2025, the renewable fresh water supply will have decreased to 235m3 per capita per annum as compared to now which is 650m3 per capita per annum (Biamah & Njeru, 2010). There is a reason to protect these existing resources as much as possible for the future generation.

This project is studying the issues of lack of water at the residents of ARM PLC, Kaloleni, identifies the possible causes of the water shortage problem and then designing an effective water distribution system through EPANET. A water distribution system is a sort of hydraulic infrastructure made up of pipes, tanks, pumps, and valves. It is crucial to provide safe drinking water to individuals, in the right quantity and at the required time. This calls for the design of an effective water distribution network or if there was an already existing water supply system, it is paramount to make more reliable and effective.  Many companies or plants have water distribution system but very few among them are aware of the water pressures within the pipes, the peak hour water demands and how to monitor a water contaminating agent incase such a scenario happens.

The water distribution design system will be through EPANET based at Athi River Mining, Kaloleni plant focusing at the employee premises and as well the water used by workers at their different work stations.

LIST OF ABBREVIATIONS

ARM-Athi River Mining

WDNs-Water Distribution Networks

NOAA-National Oceanic and Atmospheric Administration

LIST OF FIGURES

Fig 1.1 a route map from Mombasa Town to ARM Kaloleni

Fig. 1.2 a map showing ARM Cement Company

Fig. 1.3 Climatic Graph of Kilifi County

Fig. 1.4 a picture of water situation at Kilifi County

Fig. 1.5 a picture of EPANET console

Fig. 1.6 Picture of EPANET components

Fig. 1.7 Centrifugal application pump picture

Fig. 1.8 picture of water meters

Fig. 1.9 Picture of EPANET nodes and links

Fig. 2.0 Elevation profile of managers residents

Fig. 2.1 Elevation profile of couples residents

Fig. 2.2 EPANET success RUN

Fig. 2.3 Picture of Links and Nodes parameters

Fig. 2.4 Picture showing pressure variation for junction JU13

Fig. 2.5 Picture of pressures at different Junctions

LIST OF SYMBOLS

A              -            Area

Cω         -           Coefficient of Discharge.

Cr           -           Runoff Coefficient.

e             -           Exponential

Ep         -           Pump Efficiency

g             -            Acceleration due to gravity

KW         -            Kilo-Watt

KWh       -            Kilo-Watt hour L             -            Length

m            -          Meters

M³/sec.   -          Cubic meters per Second.

n             -            Manning

Pp         -            Pump Power Requirement

Q            -            Discharge

S            -            Slope

Tc           -            Time of Concentration

V             -           Velocity

𝛴           -         Summation

Table of Contents

1.0 Introduction	10

1.1 Background Information	10

1.2 PROBLEM STATEMENT	13

1.3 JUSTIFICATION	13

1.4 SITE ANALYSIS AND INVENTORY	15

1.4.2 Climate	18

1.5 OBJECTIVES	19

1.5.1 OVERALL OBJECTIVE	19

1.5.2 Specific objectives	19

1.6 Statement of Scope	19

2.0 LITERATURE REVIEW	20

2.1 Theory of Water Distribution Network Analysis	20

2.2 Introduction to EPANET	22

2.3 Components of EPANET water distribution system	24

2.3.1 Junctions	24

2.3.2 Reservoirs	25

2.3.3 Tanks	26

2.3.4 Emitters	26

2.3.5 Pipes	27

3.0 Theoretical considerations	29

3.1Population	29

3.2 Amount of water for the households	29

3.3 Water system losses	29

3.4 Pipes diameter	29

3.5 Pumps	30

3.5.1. Use of gravity	30

3.5.2. Use of pumps	30

3.5.3 Setting up of a pump	32

4.0 Methodology	35

4.1 Population	35

4.2 CALCULATION OF PIPE DIAMETERS	35

4.3 Continuity Formula	36

4.4 Energy Conservation Formula	36

4.5 Determination of the Nodal demands	37

5.0 Data analysis	38

5.1 Population estimation	38

5.2 Nodal Demand Estimations	38

5.2.1 Population Demand	38

5.2.2 Fire Demand	39

5.2.3 Minor Losses	39

5.2.4 Unaccounted for Water (UFW	39

5.3 Design of an application System	39

5.3.1 Selection of the Pump	39

5.4 Pipe sizing	42

5.5 Calculation of the diameter	42

5.6 Nodal variables	44

6.0 Results and discussions	47

6.1 Bill of quantities	50

6.2 Cost benefit analysis	50

7.0 Conclusion and Recommendations	51

7.1 Conclusion	51

7.2 Recommendation	51

8.0 Reference	52

LIST OF APPENDICES	53

# 1.0 Introduction

## 1.1 Background Information

Looking back at history, the practice of water transportation for human consumption has been in existence for millennia. From the first pipes in Crete some 3,500 years ago to today’s complex hydraulic models, the history of water distribution technology is quite a story. Water distribution systems (WDNs) have served to serve various purposes in the human history in addition to the provision of water for human use, which approximately accounts for less than 3% of the total volume of water supplied (Arnalich, 2011). Piped water has various uses including sanitation, irrigation, firefighting, and washing. Usually, networks are designed in order to meet peak demands; in parts of such network, a low flow situation is created contributing to the deterioration of microorganism and chemical quality of water.

Pipe system serves to supply water at adequate pressure heads. However, the intended pressure is not always achieved because of friction forces between the water and the pipe walls. This pressure loss effect is also dependent on the pipe length, gradient, pipe diameter and water demand. Many empirical equations have been established to describe water pressure-flow relations (Webber, 1971) and these relationships have been incorporated into water modeling software packages to facilitate their efficient usage and solution provision. To date, there is still no convenient evaluation of water distribution systems reliability. Traditionally, any water distribution design system is based on the plan of the proposed street and the slope of the land. By use of the available commercial software, the modeler stimulates pressures and flows in the network and flows in and out of the tanks for essential loadings.

Water distribution networks have a major role that they play in the modern societies since their mode of operation is related directly to people well-being.  Water supply activities, however, tend to be somewhat natural monopolies, hence to guarantee providence of good services in sustainable ways, the water distribution system performance has to be evaluated. The inclusion of performance assessment methods in management practice produces competition leading to a culture of efficiency and pursuit of unending improvement. Water utilities have the primary duty of ensuring that the required water quantity to specific customers under the necessary pressures is delivered through a distribution system.

Drinking water distribution through the distribution systems is a technical challenge both quantitatively and qualitatively. This means that every point of the network has an invariable water flow complying with all the quantitative and qualitative parameters. Water supply in Athi River Cement plant specifically within the residence premise is usually available for few hours, sometimes dirty and one end up having to wait for some time before clean water starts flowing out. This leads to wastage of the scarce water. The flow outs are usually of very low pressure and it’s unpredictable. These problems impose financial costs on the employees because they have to buy water from the nearby borehole water sellers as well as health costs.

Fig. 1.4 a picture of water situation at Kilifi County

Source: Daily Nation, June 6, 2016

## According to this post by the Daily Nation, Mombasa, Kilifi, and Kwale counties are facing a water crisis situation. A statistical analysis from the Daily print indicated that Mombasa receives only 48 million Litters of water a day from its neighbors against its demand of 200 million litters a day. This result in a deficit of 152 million liters of water a day hence the little amount that is available needs to be used efficiently and effectively. This water shortage is attributed to the county’s lack of fresh water sources forcing them to depend solely on piped water supply.